## 1
1. Valve feedback. P&F Proximity Sensors NJ2-V3-N |  | IS Loop Calculation | Tag number: XZSH/L-001, XZSH/L-004, XZSH/L-006
Barrier/Isolator detail
Manufacturer | Siemens |  | Gas/Dust | GD
Model | 6ES7 321-7RD00-0AB0 |  | Gas Group | IIC
Certification Code | II 3 G (2) GD Ex nA [ib Gb] [ib IIIC Db] IIC T4 Gc
|  |  | Uo V | Io mA | Po W | C mf | L mH
Certificate Number | KEMA 01 ATEX 1057 X |  | 10 | 14.1 | 0.0337 | 3 | 100
For two channel barriers the combined voltage, current and
power need to be calculated, refer to MTL if required.
Cable Parameters
Total
Length, metres | 5
Capacitance, mf/m | 0.0002 |  |  |  | 0.001 | mf
Inductance, mH/m | 0.001 |  |  |  | 0.005 | mH
Cable Parameters
Total
Length, metres | 100
Capacitance, mf/m | 0.00011 |  |  |  | 0.011 | mf
Inductance, mH/m | 0.00067 |  |  |  | 0.067 | mH
Cable Parameters
Total
Length, metres | 0
Capacitance, mf/m | 0 |  |  |  | 0 | mf
Inductance, mH/m | 0 |  |  |  | 0 | mH
Field Equipment Detail |  |  | Simple Apparatus? If so enter Y
|  |  | Ui V | Ii mA | Pi W | Ci mf | Li mH
Manufacturer | Pepperll and Fuchs |  | 16 | 25 | 0.064 | 0.04 | 0.05 | 16 | 25 | 0.064
Model | NJ 2-V3-N |  | Gas/Dust | G |  | 0.052 | 0.122
Certification Code | Eex ia IIC T6 |  | 'OK' | 'OK' | 'OK' | 'OK' | 'OK'
Certificate Number | Nemko 04ATEX1233 X
System suitable for: |  | IIC
Temperature rating: |  | T6
This document is provided for Customer use and assistance. However please be aware the MTL shall have no liability whatsoever in connection with this document.
NOTES: Calculated for: 5mtrs internal wiring capacitance and inductance figures as per IEC 60079-14, 16.2.2.2 100mtrs Draka RFOU(i) 150/250(300)V NEK TS 606 Code S1/S5 Manufacture: Draka Max Cable length: Calculated for 100m
JB's if fitted